## Summary
University building decarbonisation
20 fictional buildings. Annual steady-state analysis in 2026 prices. Start with Assumptions, then Buildings.
Portfolio metric | Value | Unit
Buildings | 20 | count
Capital investment | 21907737.6 | £
Baseline OPEX | 6771180 | £/yr
Proposed OPEX | 6447576.8368 | £/yr
Annual OPEX saving | 323603.1632 | £/yr
Baseline emissions | 6502.162 | tCO2e/yr
Proposed emissions | 3355.513 | tCO2e/yr
Emissions saved | 3146.649 | tCO2e/yr
Emissions reduction | 48.39% | %
Heat-pump units | 78 | count
Additional peak electricity | 3120 | kWe
Sum of site shortfalls | 2080 | kWe
Portfolio simple payback | 67.6994 | years
Cluster | CAPEX £ | OPEX saving £/yr | Emissions saved t/yr | HP units | Additional peak kWe | Site shortfalls kWe
North | 4932614.4 | 57551.2983 | 679.8043 | 19 | 760 | 500
Central | 6210355.2 | 90701.0457 | 911.7325 | 22 | 880 | 620
South | 4997395.2 | 85382.4311 | 753.7847 | 17 | 680 | 420
West | 5767372.8 | 89968.3881 | 801.3275 | 20 | 800 | 540
Energy totals
Metric | Baseline kWh/yr | Proposed kWh/yr
Useful heat | 15921600 | 13009760
Gas purchased | 19000000 | 0
Grid electricity | 23200000 | 25622426.9148
Heat-pump electricity | 0 | 4069651.9148
PV self-used | 0 | 1647225
Useful heat = gas × boiler efficiency. Heat-pump electricity = reduced useful heat ÷ seasonal COP.
CAPEX = upfront investment. OPEX = annual energy bills plus modelled plant maintenance.
Cluster peaks are sums without diversity. Spare capacity cannot automatically transfer between buildings.
Payback excludes financing, future tariff changes, equipment replacements and residual values.
Use QA to review input validity and reconciliations. Review engineering limits in Guide and sources.

## Assumptions
Editable programme assumptions
Prices include CCL and exclude VAT. Planning costs and engineering assumptions are illustrative. Research date: 25 October 2026.
Driver | Value | Unit | Basis | Source ID | Use / limitation
Electricity benchmark | 24.51 | p/kWh | DESNZ Q2 2026 all bands | S02 | Rounded from 24.50920275. Fully delivered average, not a marginal tariff.
Gas benchmark | 5.28 | p/kWh GCV | DESNZ Q2 2026 all bands | S02 | Rounded from 5.27689274. Replace with university contract values.
Gas combustion factor | 0.18231 | kgCO2e/kWh GCV | DESNZ 2026 Fuels!D42 | S01 | Scope 1. Includes CO2, CH4 and N2O.
Electricity factor | 0.13096 | kgCO2e/kWh | DESNZ 2026 UK electricity!E25 | S01 | Scope 2 location-based. Excludes transmission losses and upstream fuels.
PV annual yield | 900 | kWh/kWp/yr | Planning assumption | P01 | Annual output before self-use. No shading or hourly matching model.
SCOP multiplier | 1 | multiplier | Planning assumption | P01 | Multiplies each building seasonal COP. Use to test annual performance.
Unit heat-pump capacity | 100 | kWt/unit | Planning assumption | P01 | Delivered heat at design conditions. Rounded up, no standby redundancy.
Design COP | 2.5 | kWt/kWe | Planning assumption | P01 | Used for peak electrical demand. Separate from annual seasonal COP.
Installed HP cost | 1000 | £/kWt installed | Planning allowance | P01 | Plant, installation, emitters and integration allowance. Replace with quotations.
PV installation cost | 1100 | £/kWp | Planning allowance | P01 | No battery. No grant or export income.
Fabric works cost | 160 | £/treated m² | Planning allowance | P01 | Applied to treated area, not automatically to total building floor area.
Electrical upgrade cost | 450 | £/kWe shortfall | Planning allowance | P01 | Linear screening allowance. Does not model transformer step costs.
Professional fees | 12% | fraction of direct cost | Planning allowance | P01 | Added to direct works subtotal.
Contingency | 20% | fraction of works + fees | Planning allowance | P01 | Applied after fees. Excludes VAT, grants and financing.
Existing heating maintenance | 10 | £/baseline kWt/yr | Planning allowance | P01 | Heating plant maintenance only. Other existing maintenance cancels.
HP maintenance | 18 | £/installed kWt/yr | Planning allowance | P01 | Fixed capacity-based annual maintenance.
PV maintenance | 12 | £/kWp/yr | Planning allowance | P01 | Fabric maintenance excluded.
Portfolio price ratio | 4.642 | electricity / gas | Calculated | S02 | Heat-pump bill savings depend strongly on this ratio.
Colour key
Amber / blue text = editable input
White or pale blue = formula result
S01–S02: official sources. P01: explicit planning assumptions. See Guide and sources for links and exclusions.

## Energy
Annual energy, OPEX and emissions
Full gas-to-heat-pump conversion. Positive savings mean a reduction. All values are annual. Post-project gas is zero.
Building ID | Building | Cluster | Gas input kWh | Other electricity kWh | Boiler efficiency | Useful heat kWh | Heat reduction | Post heat kWh | Active SCOP | HP electricity kWh | PV kWp | PV generation kWh | PV self-used kWh | PV exported kWh | Grid import kWh | Baseline Scope 1 tCO2e | Baseline Scope 2 tCO2e | Baseline total tCO2e | Post Scope 2 tCO2e | Emissions saved tCO2e | Emissions reduction | Baseline energy £/yr | Post energy £/yr | Bill saving £/yr | Baseline maintenance £/yr | Post maintenance £/yr | Baseline OPEX £/yr | Post OPEX £/yr | OPEX saving £/yr
B01 | Alder Library | North | 620000 | 490000 | 82% | 508400 | 18% | 416888 | 3.3 | 126329.697 | 90 | 81000 | 64800 | 16200 | 551529.697 | 113.0322 | 64.1704 | 177.2026 | 72.2283 | 104.9743 | 59.24% | 152835 | 135179.9287 | 17655.0713 | 3150 | 6480 | 155985 | 141659.9287 | 14325.0713
B02 | Birch Teaching Centre | North | 510000 | 320000 | 86% | 438600 | 22% | 342108 | 3.4 | 100620 | 75 | 67500 | 50625 | 16875 | 369995 | 92.9781 | 41.9072 | 134.8853 | 48.4545 | 86.4308 | 64.08% | 105360 | 90685.7745 | 14674.2255 | 2520 | 6300 | 107880 | 96985.7745 | 10894.2255
B03 | Cedar Chemistry Lab | North | 1680000 | 2840000 | 80% | 1344000 | 12% | 1182720 | 2.9 | 407834.4828 | 150 | 135000 | 128250 | 6750 | 3119584.4828 | 306.2808 | 371.9264 | 678.2072 | 408.5408 | 269.6664 | 39.76% | 784788 | 764610.1567 | 20177.8433 | 7480 | 14400 | 792268 | 779010.1567 | 13257.8433
B04 | Dove Administration | North | 310000 | 210000 | 88% | 272800 | 25% | 204600 | 3.5 | 58457.1429 | 40 | 36000 | 25200 | 10800 | 243257.1429 | 56.5161 | 27.5016 | 84.0177 | 31.857 | 52.1607 | 62.08% | 67839 | 59622.3257 | 8216.6743 | 1560 | 4080 | 69399 | 63702.3257 | 5696.6743
B05 | Elm Residence | North | 1020000 | 460000 | 84% | 856800 | 16% | 719712 | 3.1 | 232165.1613 | 110 | 99000 | 84150 | 14850 | 608015.1613 | 185.9562 | 60.2416 | 246.1978 | 79.6257 | 166.5721 | 67.66% | 166602 | 149024.516 | 17577.484 | 4320 | 8520 | 170922 | 157544.516 | 13377.484
B06 | Fern Engineering | Central | 1390000 | 1530000 | 82% | 1139800 | 18% | 934636 | 3.3 | 283223.0303 | 180 | 162000 | 129600 | 32400 | 1683623.0303 | 253.4109 | 200.3688 | 453.7797 | 220.4873 | 233.2924 | 51.41% | 448395 | 412656.0047 | 35738.9953 | 5700 | 11160 | 454095 | 423816.0047 | 30278.9953
B07 | Grove Humanities | Central | 470000 | 260000 | 86% | 404200 | 22% | 315276 | 3.4 | 92728.2353 | 60 | 54000 | 40500 | 13500 | 312228.2353 | 85.6857 | 34.0496 | 119.7353 | 40.8894 | 78.8459 | 65.85% | 88542 | 76527.1405 | 12014.8595 | 2240 | 4320 | 90782 | 80847.1405 | 9934.8595
B08 | Hazel Sports Centre | Central | 1750000 | 860000 | 80% | 1400000 | 12% | 1232000 | 2.9 | 424827.5862 | 140 | 126000 | 119700 | 6300 | 1165127.5862 | 319.0425 | 112.6256 | 431.6681 | 152.5851 | 279.083 | 64.65% | 303186 | 285572.7714 | 17613.2286 | 7150 | 14280 | 310336 | 299852.7714 | 10483.2286
B09 | Iris Computing | Central | 450000 | 2380000 | 88% | 396000 | 25% | 297000 | 3.5 | 84857.1429 | 120 | 108000 | 75600 | 32400 | 2389257.1429 | 82.0395 | 311.6848 | 393.7243 | 312.8971 | 80.8272 | 20.53% | 607098 | 585606.9257 | 21491.0743 | 3120 | 6840 | 610218 | 592446.9257 | 17771.0743
B10 | Juniper Research | Central | 1460000 | 2490000 | 84% | 1226400 | 16% | 1030176 | 3.1 | 332314.8387 | 170 | 153000 | 130050 | 22950 | 2692264.8387 | 266.1726 | 326.0904 | 592.263 | 352.579 | 239.684 | 40.47% | 687387 | 659874.112 | 27512.888 | 5760 | 11040 | 693147 | 670914.112 | 22232.888
B11 | Kingfisher Hall | South | 780000 | 350000 | 82% | 639600 | 18% | 524472 | 3.3 | 158930.9091 | 85 | 76500 | 61200 | 15300 | 447730.9091 | 142.2018 | 45.836 | 188.0378 | 58.6348 | 129.403 | 68.82% | 126969 | 109738.8458 | 17230.1542 | 2930 | 6420 | 129899 | 116158.8458 | 13740.1542
B12 | Larch Medical Sciences | South | 2050000 | 3620000 | 86% | 1763000 | 22% | 1375140 | 3.4 | 404452.9412 | 200 | 180000 | 135000 | 45000 | 3889452.9412 | 373.7355 | 474.0752 | 847.8107 | 509.3628 | 338.4479 | 39.92% | 995502 | 953304.9159 | 42197.0841 | 5950 | 11400 | 1001452 | 964704.9159 | 36747.0841
B13 | Maple Arts Studio | South | 390000 | 290000 | 80% | 312000 | 12% | 274560 | 2.9 | 94675.8621 | 55 | 49500 | 47025 | 2475 | 337650.8621 | 71.1009 | 37.9784 | 109.0793 | 44.2188 | 64.8605 | 59.46% | 91671 | 82758.2263 | 8912.7737 | 2970 | 6060 | 94641 | 88818.2263 | 5822.7737
B14 | Newton Lecture Block | South | 690000 | 440000 | 88% | 607200 | 25% | 455400 | 3.5 | 130114.2857 | 100 | 90000 | 63000 | 27000 | 507114.2857 | 125.7939 | 57.6224 | 183.4163 | 66.4117 | 117.0046 | 63.79% | 144276 | 124293.7114 | 19982.2886 | 2990 | 6600 | 147266 | 130893.7114 | 16372.2886
B15 | Oak Student Centre | South | 620000 | 610000 | 84% | 520800 | 16% | 437472 | 3.1 | 141120 | 95 | 85500 | 72675 | 12825 | 678445 | 113.0322 | 79.8856 | 192.9178 | 88.8492 | 104.0686 | 53.94% | 182247 | 166286.8695 | 15960.1305 | 3280 | 6540 | 185527 | 172826.8695 | 12700.1305
B16 | Pine Archives | West | 280000 | 170000 | 82% | 229600 | 18% | 188272 | 3.3 | 57052.1212 | 35 | 31500 | 25200 | 6300 | 201852.1212 | 51.0468 | 22.2632 | 73.31 | 26.4346 | 46.8754 | 63.94% | 56451 | 49473.9549 | 6977.0451 | 1650 | 4020 | 58101 | 53493.9549 | 4607.0451
B17 | Quartz Physics | West | 1920000 | 3150000 | 86% | 1651200 | 22% | 1287936 | 3.4 | 378804.7059 | 210 | 189000 | 141750 | 47250 | 3387054.7059 | 350.0352 | 412.524 | 762.5592 | 443.5687 | 318.9905 | 41.83% | 873441 | 830167.1084 | 43273.8916 | 6370 | 13320 | 879811 | 843487.1084 | 36323.8916
B18 | Rowan Graduate House | West | 610000 | 280000 | 80% | 488000 | 12% | 429440 | 2.9 | 148082.7586 | 65 | 58500 | 55575 | 2925 | 372507.7586 | 111.2091 | 36.6688 | 147.8779 | 48.7836 | 99.0943 | 67.01% | 100836 | 91301.6516 | 9534.3484 | 3630 | 7980 | 104466 | 99281.6516 | 5184.3484
B19 | Sycamore Workshop | West | 1080000 | 790000 | 88% | 950400 | 25% | 712800 | 3.5 | 203657.1429 | 125 | 112500 | 78750 | 33750 | 914907.1429 | 196.8948 | 103.4584 | 300.3532 | 119.8162 | 180.537 | 60.11% | 250653 | 224243.7407 | 26409.2593 | 3770 | 6900 | 254423 | 231143.7407 | 23279.2593
B20 | Willow Innovation | West | 920000 | 1660000 | 84% | 772800 | 16% | 649152 | 3.1 | 209403.871 | 155 | 139500 | 118575 | 20925 | 1750828.871 | 167.7252 | 217.3936 | 385.1188 | 229.2885 | 155.8303 | 40.46% | 455442 | 429128.1563 | 26313.8437 | 5120 | 10860 | 460562 | 439988.1563 | 20573.8437
| Portfolio total |  | 19000000 | 23200000 |  | 15921600 |  | 13009760 |  | 4069651.9148 | 2260 | 2034000 | 1647225 | 386775 | 25622426.9148 | 3463.89 | 3038.272 | 6502.162 | 3355.513 | 3146.649 | 48.39% | 6689520 | 6280056.8368 | 409463.1632 | 81660 | 167520 | 6771180 | 6447576.8368 | 323603.1632

## CAPEX
Equipment, electrical capacity and capital cost
Peak electrical demand uses design COP and rounded installed capacity. PV provides no winter peak credit. Costs exclude VAT.
Building ID | Building | Cluster | Post design heat kWt | Unit capacity kWt | HP unit count | Installed heat kWt | Design COP | Additional peak kWe | Spare capacity kWe | Shortfall kWe | HP installation £ | Electrical upgrade £ | PV installation £ | Fabric works £ | Direct subtotal £ | Fees £ | Contingency £ | Total CAPEX £ | OPEX saving £/yr | Simple payback years | CAPEX / annual tCO2e saved
B01 | Alder Library | North | 267.75 | 100 | 3 | 300 | 2.5 | 120 | 55 | 65 | 300000 | 29250 | 99000 | 201600 | 629850 | 75582 | 141086.4 | 846518.4 | 14325.0713 | 59.0935 | 8064.056
B02 | Birch Teaching Centre | North | 201.6 | 100 | 3 | 300 | 2.5 | 120 | 40 | 80 | 300000 | 36000 | 82500 | 201600 | 620100 | 74412 | 138902.4 | 833414.4 | 10894.2255 | 76.5006 | 9642.5676
B03 | Cedar Chemistry Lab | North | 673.2 | 100 | 7 | 700 | 2.5 | 280 | 90 | 190 | 700000 | 85500 | 165000 | 217600 | 1168100 | 140172 | 261654.4 | 1569926.4 | 13257.8433 | 118.4149 | 5821.735
B04 | Dove Administration | North | 121.68 | 100 | 2 | 200 | 2.5 | 80 | 25 | 55 | 200000 | 24750 | 44000 | 153600 | 422350 | 50682 | 94606.4 | 567638.4 | 5696.6743 | 99.6438 | 10882.4827
B05 | Elm Residence | North | 367.2 | 100 | 4 | 400 | 2.5 | 160 | 50 | 110 | 400000 | 49500 | 121000 | 259200 | 829700 | 99564 | 185852.8 | 1115116.8 | 13377.484 | 83.3577 | 6694.4979
B06 | Fern Engineering | Central | 484.5 | 100 | 5 | 500 | 2.5 | 200 | 55 | 145 | 500000 | 65250 | 198000 | 364800 | 1128050 | 135366 | 252683.2 | 1516099.2 | 30278.9953 | 50.071 | 6498.7073
B07 | Grove Humanities | Central | 179.2 | 100 | 2 | 200 | 2.5 | 80 | 40 | 40 | 200000 | 18000 | 66000 | 179200 | 463200 | 55584 | 103756.8 | 622540.8 | 9934.8595 | 62.6623 | 7895.6658
B08 | Hazel Sports Centre | Central | 643.5 | 100 | 7 | 700 | 2.5 | 280 | 90 | 190 | 700000 | 85500 | 154000 | 208000 | 1147500 | 137700 | 257040 | 1542240 | 10483.2286 | 147.115 | 5526.0981
B09 | Iris Computing | Central | 243.36 | 100 | 3 | 300 | 2.5 | 120 | 25 | 95 | 300000 | 42750 | 132000 | 307200 | 781950 | 93834 | 175156.8 | 1050940.8 | 17771.0743 | 59.1377 | 13002.3185
B10 | Juniper Research | Central | 489.6 | 100 | 5 | 500 | 2.5 | 200 | 50 | 150 | 500000 | 67500 | 187000 | 345600 | 1100100 | 132012 | 246422.4 | 1478534.4 | 22232.888 | 66.5021 | 6168.6822
B11 | Kingfisher Hall | South | 249.05 | 100 | 3 | 300 | 2.5 | 120 | 55 | 65 | 300000 | 29250 | 93500 | 187200 | 609950 | 73194 | 136628.8 | 819772.8 | 13740.1542 | 59.6626 | 6335.039
B12 | Larch Medical Sciences | South | 476 | 100 | 5 | 500 | 2.5 | 200 | 40 | 160 | 500000 | 72000 | 220000 | 476000 | 1268000 | 152160 | 284032 | 1704192 | 36747.0841 | 46.3763 | 5035.315
B13 | Maple Arts Studio | South | 267.3 | 100 | 3 | 300 | 2.5 | 120 | 90 | 30 | 300000 | 13500 | 60500 | 86400 | 460400 | 55248 | 103129.6 | 618777.6 | 5822.7737 | 106.2685 | 9540.1236
B14 | Newton Lecture Block | South | 233.22 | 100 | 3 | 300 | 2.5 | 120 | 25 | 95 | 300000 | 42750 | 110000 | 294400 | 747150 | 89658 | 167361.6 | 1004169.6 | 16372.2886 | 61.3335 | 8582.3078
B15 | Oak Student Centre | South | 278.8 | 100 | 3 | 300 | 2.5 | 120 | 50 | 70 | 300000 | 31500 | 104500 | 196800 | 632800 | 75936 | 141747.2 | 850483.2 | 12700.1305 | 66.9665 | 8172.3291
B16 | Pine Archives | West | 140.25 | 100 | 2 | 200 | 2.5 | 80 | 55 | 25 | 200000 | 11250 | 38500 | 105600 | 355350 | 42642 | 79598.4 | 477590.4 | 4607.0451 | 103.6652 | 10188.4982
B17 | Quartz Physics | West | 509.6 | 100 | 6 | 600 | 2.5 | 240 | 40 | 200 | 600000 | 90000 | 231000 | 509600 | 1430600 | 171672 | 320454.4 | 1922726.4 | 36323.8916 | 52.9328 | 6027.5347
B18 | Rowan Graduate House | West | 326.7 | 100 | 4 | 400 | 2.5 | 160 | 90 | 70 | 400000 | 31500 | 71500 | 105600 | 608600 | 73032 | 136326.4 | 817958.4 | 5184.3484 | 157.7746 | 8254.3449
B19 | Sycamore Workshop | West | 294.06 | 100 | 3 | 300 | 2.5 | 120 | 25 | 95 | 300000 | 42750 | 137500 | 371200 | 851450 | 102174 | 190724.8 | 1144348.8 | 23279.2593 | 49.1574 | 6338.5846
B20 | Willow Innovation | West | 435.2 | 100 | 5 | 500 | 2.5 | 200 | 50 | 150 | 500000 | 67500 | 170500 | 307200 | 1045200 | 125424 | 234124.8 | 1404748.8 | 20573.8437 | 68.2784 | 9014.6091
| Portfolio total |  | 6881.77 |  | 78 | 7800 |  | 3120 | 1040 | 2080 | 7800000 | 936000 | 2486000 | 5078400 | 16300400 | 1956048 | 3651289.6 | 21907737.6 | 323603.1632 | 67.6994 | 6962.2439

## Consultant
Standardised consultant tariff comparison
Invented consultant rates. Identical modelled kWh under both price sets isolates tariff effects. Energy bills only, excluding maintenance.
Building ID | Fictional consultant | Gas p/kWh | Electricity p/kWh | Baseline gas kWh | Baseline electricity kWh | Post grid kWh | Own-rate baseline £ | Own-rate post £ | Own-rate bill saving £ | Common baseline £ | Common post £ | Common bill saving £ | Baseline repricing £ | Post repricing £ | Saving adjustment £ | Bridge residual £
B01 | Atlas Demo | 4.2 | 19.5 | 620000 | 490000 | 551529.697 | 121590 | 107548.2909 | 14041.7091 | 152835 | 135179.9287 | 17655.0713 | 31245 | 27631.6378 | 3613.3622 | 0
B02 | Atlas Demo | 4.2 | 19.5 | 510000 | 320000 | 369995 | 83820 | 72149.025 | 11670.975 | 105360 | 90685.7745 | 14674.2255 | 21540 | 18536.7495 | 3003.2505 | 0
B03 | Atlas Demo | 4.2 | 19.5 | 1680000 | 2840000 | 3119584.4828 | 624360 | 608318.9741 | 16041.0259 | 784788 | 764610.1567 | 20177.8433 | 160428 | 156291.1826 | 4136.8174 | 0
B04 | Atlas Demo | 4.2 | 19.5 | 310000 | 210000 | 243257.1429 | 53970 | 47435.1429 | 6534.8571 | 67839 | 59622.3257 | 8216.6743 | 13869 | 12187.1829 | 1681.8171 | 0
B05 | Atlas Demo | 4.2 | 19.5 | 1020000 | 460000 | 608015.1613 | 132540 | 118562.9565 | 13977.0435 | 166602 | 149024.516 | 17577.484 | 34062 | 30461.5596 | 3600.4404 | 0
B06 | Beacon Demo | 6.1 | 31 | 1390000 | 1530000 | 1683623.0303 | 559090 | 521923.1394 | 37166.8606 | 448395 | 412656.0047 | 35738.9953 | -110695 | -109267.1347 | -1427.8653 | 0
B07 | Beacon Demo | 6.1 | 31 | 470000 | 260000 | 312228.2353 | 109270 | 96790.7529 | 12479.2471 | 88542 | 76527.1405 | 12014.8595 | -20728 | -20263.6125 | -464.3875 | 0
B08 | Beacon Demo | 6.1 | 31 | 1750000 | 860000 | 1165127.5862 | 373350 | 361189.5517 | 12160.4483 | 303186 | 285572.7714 | 17613.2286 | -70164 | -75616.7803 | 5452.7803 | 0
B09 | Beacon Demo | 6.1 | 31 | 450000 | 2380000 | 2389257.1429 | 765250 | 740669.7143 | 24580.2857 | 607098 | 585606.9257 | 21491.0743 | -158152 | -155062.7886 | -3089.2114 | 0
B10 | Beacon Demo | 6.1 | 31 | 1460000 | 2490000 | 2692264.8387 | 860960 | 834602.1 | 26357.9 | 687387 | 659874.112 | 27512.888 | -173573 | -174727.988 | 1154.988 | 0
B11 | Campus Demo | 5.8 | 27.5 | 780000 | 350000 | 447730.9091 | 141490 | 123126 | 18364 | 126969 | 109738.8458 | 17230.1542 | -14521 | -13387.1542 | -1133.8458 | 0
B12 | Campus Demo | 5.8 | 27.5 | 2050000 | 3620000 | 3889452.9412 | 1114400 | 1069599.5588 | 44800.4412 | 995502 | 953304.9159 | 42197.0841 | -118898 | -116294.6429 | -2603.3571 | 0
B13 | Campus Demo | 5.8 | 27.5 | 390000 | 290000 | 337650.8621 | 102370 | 92853.9871 | 9516.0129 | 91671 | 82758.2263 | 8912.7737 | -10699 | -10095.7608 | -603.2392 | 0
B14 | Campus Demo | 5.8 | 27.5 | 690000 | 440000 | 507114.2857 | 161020 | 139456.4286 | 21563.5714 | 144276 | 124293.7114 | 19982.2886 | -16744 | -15162.7171 | -1581.2829 | 0
B15 | Campus Demo | 5.8 | 27.5 | 620000 | 610000 | 678445 | 203710 | 186572.375 | 17137.625 | 182247 | 166286.8695 | 15960.1305 | -21463 | -20285.5055 | -1177.4945 | 0
B16 | Delta Demo | 4.8 | 22 | 280000 | 170000 | 201852.1212 | 50840 | 44407.4667 | 6432.5333 | 56451 | 49473.9549 | 6977.0451 | 5611 | 5066.4882 | 544.5118 | 0
B17 | Delta Demo | 4.8 | 22 | 1920000 | 3150000 | 3387054.7059 | 785160 | 745152.0353 | 40007.9647 | 873441 | 830167.1084 | 43273.8916 | 88281 | 85015.0731 | 3265.9269 | 0
B18 | Delta Demo | 4.8 | 22 | 610000 | 280000 | 372507.7586 | 90880 | 81951.7069 | 8928.2931 | 100836 | 91301.6516 | 9534.3484 | 9956 | 9349.9447 | 606.0553 | 0
B19 | Delta Demo | 4.8 | 22 | 1080000 | 790000 | 914907.1429 | 225640 | 201279.5714 | 24360.4286 | 250653 | 224243.7407 | 26409.2593 | 25013 | 22964.1693 | 2048.8307 | 0
B20 | Delta Demo | 4.8 | 22 | 920000 | 1660000 | 1750828.871 | 409360 | 385182.3516 | 24177.6484 | 455442 | 429128.1563 | 26313.8437 | 46082 | 43945.8047 | 2136.1953 | 0
| Portfolio total |  |  | 19000000 | 23200000 | 25622426.9148 | 6969070 | 6578771.1291 | 390298.8709 | 6689520 | 6280056.8368 | 409463.1632 | -279550 | -298714.2922 | 19164.2922 | 0

## Buildings
Fictional building register
Amber cells are editable. All buildings, surveys, capacities and study references are invented training data.
Building ID | Building | Cluster | Use | Floor area m² | Gas input kWh/yr GCV | Other electricity kWh/yr | Boiler efficiency GCV | Annual heat reduction | Baseline design heat kWt | Peak heat reduction | Seasonal COP | Proposed PV kWp | PV self-use fraction | Fabric treated m² | Spare capacity kWe | Project stage | Fictional study ref
B01 | Alder Library | North | Library | 4200 | 620000 | 490000 | 82% | 18% | 315 | 15% | 3.3 | 90 | 80% | 1260 | 55 | Feasibility | DEMO-FS-01
B02 | Birch Teaching Centre | North | Teaching | 3600 | 510000 | 320000 | 86% | 22% | 252 | 20% | 3.4 | 75 | 75% | 1260 | 40 | Survey | DEMO-FS-02
B03 | Cedar Chemistry Lab | North | Laboratory | 6800 | 1680000 | 2840000 | 80% | 12% | 748 | 10% | 2.9 | 150 | 95% | 1360 | 90 | Design | DEMO-FS-03
B04 | Dove Administration | North | Office | 2400 | 310000 | 210000 | 88% | 25% | 156 | 22% | 3.5 | 40 | 70% | 960 | 25 | Feasibility | DEMO-FS-04
B05 | Elm Residence | North | Residence | 5400 | 1020000 | 460000 | 84% | 16% | 432 | 15% | 3.1 | 110 | 85% | 1620 | 50 | Survey | DEMO-FS-05
B06 | Fern Engineering | Central | Engineering | 7600 | 1390000 | 1530000 | 82% | 18% | 570 | 15% | 3.3 | 180 | 80% | 2280 | 55 | Feasibility | DEMO-FS-06
B07 | Grove Humanities | Central | Teaching | 3200 | 470000 | 260000 | 86% | 22% | 224 | 20% | 3.4 | 60 | 75% | 1120 | 40 | Survey | DEMO-FS-07
B08 | Hazel Sports Centre | Central | Sports | 6500 | 1750000 | 860000 | 80% | 12% | 715 | 10% | 2.9 | 140 | 95% | 1300 | 90 | Design | DEMO-FS-08
B09 | Iris Computing | Central | Computing | 4800 | 450000 | 2380000 | 88% | 25% | 312 | 22% | 3.5 | 120 | 70% | 1920 | 25 | Feasibility | DEMO-FS-09
B10 | Juniper Research | Central | Laboratory | 7200 | 1460000 | 2490000 | 84% | 16% | 576 | 15% | 3.1 | 170 | 85% | 2160 | 50 | Survey | DEMO-FS-10
B11 | Kingfisher Hall | South | Residence | 3900 | 780000 | 350000 | 82% | 18% | 293 | 15% | 3.3 | 85 | 80% | 1170 | 55 | Feasibility | DEMO-FS-11
B12 | Larch Medical Sciences | South | Laboratory | 8500 | 2050000 | 3620000 | 86% | 22% | 595 | 20% | 3.4 | 200 | 75% | 2975 | 40 | Survey | DEMO-FS-12
B13 | Maple Arts Studio | South | Arts | 2700 | 390000 | 290000 | 80% | 12% | 297 | 10% | 2.9 | 55 | 95% | 540 | 90 | Design | DEMO-FS-13
B14 | Newton Lecture Block | South | Teaching | 4600 | 690000 | 440000 | 88% | 25% | 299 | 22% | 3.5 | 100 | 70% | 1840 | 25 | Feasibility | DEMO-FS-14
B15 | Oak Student Centre | South | Student services | 4100 | 620000 | 610000 | 84% | 16% | 328 | 15% | 3.1 | 95 | 85% | 1230 | 50 | Survey | DEMO-FS-15
B16 | Pine Archives | West | Archive | 2200 | 280000 | 170000 | 82% | 18% | 165 | 15% | 3.3 | 35 | 80% | 660 | 55 | Feasibility | DEMO-FS-16
B17 | Quartz Physics | West | Laboratory | 9100 | 1920000 | 3150000 | 86% | 22% | 637 | 20% | 3.4 | 210 | 75% | 3185 | 40 | Survey | DEMO-FS-17
B18 | Rowan Graduate House | West | Residence | 3300 | 610000 | 280000 | 80% | 12% | 363 | 10% | 2.9 | 65 | 95% | 660 | 90 | Design | DEMO-FS-18
B19 | Sycamore Workshop | West | Workshop | 5800 | 1080000 | 790000 | 88% | 25% | 377 | 22% | 3.5 | 125 | 70% | 2320 | 25 | Feasibility | DEMO-FS-19
B20 | Willow Innovation | West | Research | 6400 | 920000 | 1660000 | 84% | 16% | 512 | 15% | 3.1 | 155 | 85% | 1920 | 50 | Survey | DEMO-FS-20

## QA
Quality assurance
Residuals should be zero within tolerance. FAIL identifies a broken check. REVIEW means a source input needs attention.
Building ID | Building | Input issues | Duplicate ID count | Heat balance kWh | Electricity balance kWh | PV balance kWh | Tariff bridge £ | CAPEX residual £ | Capacity margin kWt | Result
B01 | Alder Library | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 32.25 | PASS
B02 | Birch Teaching Centre | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 98.4 | PASS
B03 | Cedar Chemistry Lab | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 26.8 | PASS
B04 | Dove Administration | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 78.32 | PASS
B05 | Elm Residence | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 32.8 | PASS
B06 | Fern Engineering | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 15.5 | PASS
B07 | Grove Humanities | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 20.8 | PASS
B08 | Hazel Sports Centre | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 56.5 | PASS
B09 | Iris Computing | 0 | 1 | 0 | -1.3097e-10 | 0 | 0 | 0 | 56.64 | PASS
B10 | Juniper Research | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10.4 | PASS
B11 | Kingfisher Hall | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 50.95 | PASS
B12 | Larch Medical Sciences | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 24 | PASS
B13 | Maple Arts Studio | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 32.7 | PASS
B14 | Newton Lecture Block | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 66.78 | PASS
B15 | Oak Student Centre | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 21.2 | PASS
B16 | Pine Archives | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 59.75 | PASS
B17 | Quartz Physics | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 90.4 | PASS
B18 | Rowan Graduate House | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 73.3 | PASS
B19 | Sycamore Workshop | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5.94 | PASS
B20 | Willow Innovation | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 64.8 | PASS
Overall checks
Building count | PASS
Detail results | PASS
OPEX reconciliation £ | 0
Cluster CAPEX residual £ | 0
Cluster carbon residual t | 0
Numeric inputs complete | PASS
Assumption ranges | PASS
Consultant rates complete | PASS
Residual tolerances: 0.01 kWh or £ for row checks. Capacity margin must be non-negative.
PASS confirms arithmetic and listed input checks only. It does not validate a survey, quotation or connection offer.

## Guide and sources
How to use the workbook and source register
Fictional example. No actual Oxford buildings or consultant reports are represented.
Topic | Explanation
1. Edit inputs | Change amber cells in Assumptions, Buildings and Consultant. Replace fictional survey data before using real results.
2. Follow calculations | Energy shows useful heat, demand reduction, heat-pump electricity, PV, bills, maintenance and emissions.
3. Review programme | CAPEX estimates plant numbers, peak electric demand and capital costs. Summary aggregates all 20 buildings and four clusters.
4. Compare consultants | Consultant applies each invented tariff pair to the same baseline and post-project kWh. Then applies common tariffs.
5. Check QA | Check all row results and residuals. Fix missing, invalid or duplicate inputs. Formula errors remain visible.
Useful heat | Gas input × boiler efficiency, both on a gross calorific value basis. Gas is assumed to serve heating and hot water only.
Annual heat-pump demand | Useful heat × (1 − annual heat reduction) ÷ seasonal COP. SCOP includes auxiliaries and defrost in this simplified model.
Peak design | Baseline design heat × (1 − peak heat reduction). Round up to 100 kWt units. Installed kWt ÷ design COP gives peak kWe.
PV | Generation = kWp × annual yield. Self-use = MIN(generation × self-use fraction, annual total electric demand). Export has no income or carbon credit.
Cost comparison | Positive saving = baseline minus proposed. Energy bills use common p/kWh ÷ 100. OPEX adds heating/PV maintenance.
CAPEX | Direct works + professional fees + contingency on works and fees. Zero grants, no VAT, financing or inflation.
Payback | Total CAPEX ÷ positive annual OPEX saving. No saving is shown when annual OPEX saving is zero or negative.
Emissions | Scope 1 gas combustion plus Scope 2 location-based grid electricity. Post gas = 0. Factors are fixed at 2026 values for both cases.
Carbon metric | CAPEX / annual tonnes saved is £ per (tCO2e/year), not a lifetime marginal abatement cost or carbon price.
Tariff standardisation | Common saving − own-rate saving = baseline repricing − post repricing. No technical performance changes are attributed to tariffs.
Price limitations | DESNZ prices are fully delivered averages including fixed-cost elements, not marginal unit tariffs. No extra standing charge or CCL is added.
Engineering limits | No hourly simulation, N+1 standby, thermal storage, retained boilers, cooling interactions or heat-network distribution losses.
Fabric and hot water | Annual heat reduction is a blended assumption across space heat and hot water. Replace with separate demands for detailed design.
Electrical limits | Clusters are geographical reporting groups. Peaks are undiversified sums. Site shortfalls are summed without pooling spare capacity.
Uncertainty | All building demand, peak loads, COPs, PV sizes, savings, costs and maintenance are illustrative. Validate with surveys and quotations.
Emissions exclusions | No embodied carbon, refrigerant leakage, upstream fuel emissions, electricity T&D losses, market-based accounting or future grid decarbonisation.
Updates and extension | Edit the existing 20 records. Tables are filterable. Adding buildings requires extending build rows, bounded lookup ranges, QA and summaries.
Source ID | Source / evidence | URL | Published / period | Location | Use
S01 | DESNZ GHG conversion factors 2026. Full workbook downloaded and numeric cells verified. | https://www.gov.uk/government/publications/greenhouse-gas-reporting-conversion-factors-2026 | 11 Jun 2026; page updated 31 Jul 2026 | Fuels!D42; UK electricity!E25 | Gas 0.18231; electricity 0.13096 kgCO2e/kWh.
S01a | DESNZ 2026 methodology paper. Gas GCV paragraph 2.9. Electricity scope paragraph 3.1 and Table 9. | https://assets.publishing.service.gov.uk/media/6a2940543b15d05a7ce3202e/2026-GHG-conversion-factors-methodology-report.pdf | 2026 | Pages 20, 25 and 34–35 (printed) | Use gross-CV gas and Scope 2 generation factor.
S01b | Original 2026 full-set workbook. No revision to full set in July. | https://assets.publishing.service.gov.uk/media/6a29392bade52dc0882218a8/ghg-conversion-factors-2026-full-set.xlsx | 11 Jun 2026 | Fuels!D42 = 0.18231; UK electricity!E25 = 0.13096 | Exact numeric provenance for editable factors.
S02 | DESNZ non-domestic prices QEP 3.4.2. Includes CCL, excludes VAT. Q2 provisional. | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector | 29 Sep 2026; Apr–Jun 2026 | 3.4.2 (incl CCL)!J98 and P98; Notes sheet | All-band electricity 24.50920275p; gas 5.27689274p.
S02a | Underlying QEP tables downloaded and cells verified. Small/medium electricity 27.666571p; small gas 4.856000p. | https://assets.publishing.service.gov.uk/media/6ab543da997a4b2950cceedc/table_341.xlsx | 29 Sep 2026 | 3.4.2 (incl CCL)!E98 and L98 | Band prices illustrate variation. Common model uses all-band averages.
S02b | Quarterly Energy Prices September 2026, official statistical release. | https://www.gov.uk/government/statistics/quarterly-energy-prices-september-2026 | 29 Sep 2026 | Non-domestic chapter | Context and provisional price methodology.
P01 | Author-defined fictional planning assumptions and synthetic building register. | Not an external source | 25 Oct 2026 | Buildings; Consultant; Assumptions B11:B23 | Costs are allowances, not government benchmarks or supplier quotations.
Research accessed | 2026-10-25 12:00